EVALUATION OF Oxidation reduction potential (ORP) FOR WASTEWATER CHLORINATION CONTROL

Laboratory Bench Study:

This phase of the study was initiated to determine ORP values associated with the normal effective range of total combined residual chlorine concentrations obtained during actual field disinfection. This study phase was conducted prior to our seasonal requirement (May through October) for effluent disinfection. Therefore, we would have a reasonable idea what to expect when the study moved out into the field evaluation stage.

Procedure used was as follows:

Equipment used included an Oakton pH 100 series pH/mv/oC meter with ORP electrode (Ag/AgCl) for ORP analysis and a Hach Amperometric titration system for total combined residual chlorine analysis using Hach reagents.

1. Establish chlorine concentration of Bleach solution used for sample spiking - perform this occasionally

a. Measure 10 ul (0.010 ml) of bleach into 1 liter of DI water

b. perform chlorine analysis using amperometric titrator (use 0.100 ml increments of PAO until near endpoint

then cut back to 0.010 ml increments (10 uL))

c. multiply result from step b times dilution factor of 100,000 to obtain mg/L Cl2 concentration of bleach

2. Perform ORP analysis of plant effluent (untreated) - record reading and temperature

3. Prepare chlorinated plant effluent sample

a. Measure out two 200 mls aliquots of plant effluent - one for Cl2 analysis, one for ORP analysis

b. Add 10-50 ul * bleach to each sample - wait ca 9 minutes to allow initial demand to be met and simulate

time between field dosing location and filed location of initial Cl2 measurement

Nominal Dose = (mg/L Cl2 in bleach x mls bleach added) / 200 ml sample = mg/L Cl2

Aliquot 1: Cl2 analysis

a. Add Acetic Acid buffer and KI packet; put on amperometric titrator and begin stirring.

b. Add 100 ul increments of 0.00564 N PAO until amperometric reading nears 0.00.

c. Finish by adding 10 ul increments of PAO until reading holds at or near 0.00 for 3 successive additions.

mg/L Cl2 residual = mls PAO added

Aliquot 2: ORP analysis

Perform ORP analysis of plant effluent (treated) - record reading and temperature

*   depending upon Chlorine demand of sample

At bench study initiation, it was not known whether we would see an absolute ORP reading of the disinfected effluent which would indicate effective disinfection or whether we would have to rely on a differential between the chlorinated effluent’s ORP reading and the ORP reading of the effluent prior to chlorination. We therefore evaluated both possibilities with our data processing of the experimental data obtained during this bench study. Graphs indicating both control procedure possibilities follow:

The next phase of the lab bench study was initiated to determine ORP values associated with the normal effective range of sulfite concentrations obtained during actual field dechlorination with sodium bisulfite after disinfection. This would give us an indication whether we could use ORP to control the dechlorination process as well as the disinfection process. Once again, it would also give us a reasonable idea what to expect when the study moved out into the field evaluation stage.

The procedure involved taking an ORP reading on the untreated plant effluent. Then, the effluent was spiked with known amounts of a sulfite stock standard to produce sulfite concentrations at the levels normally experienced in field dechlorination. ORP readings were taken after addition of each spiking aliquot after the readings had stabilized. As with the disinfection process, we did not know if we would be able to use an absolute ORP reading or a differential between the untreated effluent and the dechlorinated effluent for control of the process. Table of laboratory results follow:

Field Phase of Study – Laboratory Data

During the field phase of the study (May-October 2006) which corresponds with the district’s NPDES permit required disinfection season, the district laboratory is required to analyze for fecal coliform and total combined chlorine residual in the plant effluent after chlorination/dechlorination two days per week. As well as these parameters, the laboratory also performed ORP analysis on samples taken at the same time as those used for fecal coliform and chlorine analysis. These included effluent prior to chlorination, effluent at front of contact tanks just after chlorination, effluent at end of contact tank just prior to dechlorination, and effluent as discharged to the Sangamon River after all treatment processes.

Several factors complicate interpretation of data which is presented at the end of this section. One was laboratory ORP analysis of the two chlorinated samples. Because of the active chlorine demand still present in these samples, readings often drifted downward as more chlorine demand was met. The laboratory attempted to analyze these samples promptly upon receipt, although sometimes there was more delay than at other times. This is where comparison needs to be made between the laboratory readings in a static sample with the field readings on a dynamic sample taken at the same time. Fecal coliform counts could also be affected by the effluent from the district’s water tower which is used to dilute the sodium bisulfite solution used for dechlorination. This effluent is chlorinated, but has been proven from past studies to add a contribution to the fecal coliform counts in the effluent of varying degree depending on its chlorine content. Cleaning processes in the plant can add to the algal content in the effluent which past district experience has shown to be a source for increasing district fecal coliform counts in the effluent even after chlorination. Incoming Fecal Coliform colonies will also increase in mid summer as the district pumps more sludge lagoons’ supernatant back to the plant in preparation for the fall land application season. Rainfall also has effects on the incoming fecal coliform counts. A significant rain after a dry spell can cause a significant elevation in fecal coliform counts due to run off from the city and surrounding area. During a continuous rainy period, the fecal coliform colony counts will often decline after the initial elevation mentioned before.

Since we had no failures of our fecal coliform permit limit during this study, it is apparent that maintenance of the ORP differential at the levels intended was effective in meeting this limit. The only time we had a total combined residual chlorine excursion was on 8/8/06 and it was determined to be due to a pump failure. This was also the only time we had a positive ORP differential between the effluent sample before chlorination and the effluent sample after chlorination/dechlorination. This would seem to indicate the effectiveness of ORP in controlling this process as well.

|  |  | FE pre | FE Channel | Change in | FE Channel | Change in | FE Channel | FE change | FE dechlor |  | FE dechlor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | FE | Chlorination | just after | ORP upon | pre de- | ORP during | after de- | in ORP from | Fecal | Fecal | Chlorine |
|  | pre Chlor | F. Coliform | Chlorination | chlorination | chlorination | contact | chlorination | prechlor to | Coliform, | Coliform, | residual, |
| Date | (mv) | # col/ 100 ml | ORP, mv | (mv) | ORP, mv | (mv) | ORP, mv | dechlor, mv | # col/ 100 ml | % Kill | (mg/L) |
| 5/2/2006 | 251 | 16000 | 397 | 146 | 357 | -40 | 209 | -42 | 39 | 99.8 | <0.011 |
| 5/4/2006 | 268 | 4600 | 435 | 167 | 429 | -6 | 225 | -43 | 10 | 99.8 | <0.011 |
| 5/9/2006 | 248 | 3700 | 400 | 152 | 374 | -26 | 208 | -40 | 14 | 99.6 | <0.011 |
| 5/11/2006 | 260 | 66000 | 445 | 185 | 414 | -31 | 225 | -35 | 24 | 100.0 | <0.011 |
| 5/16/2006 | 235 | 1900 | 396 | 161 | 364 | -32 | 210 | -25 | 27 | 98.6 | <0.011 |
| 5/18/2006 | 224 | 17000 | 390 | 166 | 345 | -45 | 213 | -11 | 43 | 99.7 | <0.011 |
| 5/23/2006 | 237 | 3300 | 362 | 125 | 319 | -43 | 188 | -49 | 55 | 98.3 | <0.011 |
| 5/25/2006 | 229 | 6600 | 404 | 175 | 369 | -35 | 203 | -26 | 17 | 99.7 | <0.011 |
| 5/30/2006 | 216 | 11000 | 336 | 120 | 292 | -44 | 178 | -38 | 27 | 99.8 | <0.011 |
| 6/1/2006 | 255 | 334000 | 443 | 188 | 431 | -12 | 202 | -53 | 14 | 100.0 | <0.011 |
| 6/6/2006 | 220 | 11000 | 352 | 132 | 321 | -31 | 194 | -26 | 9 | 99.9 | 0.020 |
| 6/8/2006 | 216 | 3100 | 348 | 132 | 313 | -35 | 186 | -30 | 10 | 99.7 | <0.011 |
| 6/15/2006 | 222 | 7200 | 368 | 146 | 282 | -86 | 187 | -35 | 36 | 99.5 | <0.011 |
| 7/5/2006 | 224 | 20000 | 354 | 130 | 263 | -91 | 195 | -29 | 74 | 99.6 | <0.011 |
| 7/11/2006 | 253 | 120000 | 433 | 180 | 437 | 4 | 212 | -41 | 2 | 100.0 | <0.011 |
| 7/13/2006 | 229 | 100000 | 395 | 166 | 366 | -29 | 190 | -39 | 29 | 100.0 | <0.011 |
| 7/18/2006 | 207 | 3100 | 274 | 67 | 264 | -10 | 179 | -28 | 11 | 99.6 | <0.011 |
| 7/20/2006 | 213 | 2400 | 377 | 164 | 294 | -83 | 169 | -44 | 34 | 98.6 | <0.011 |
| 7/25/2006 | 212 | 35000 | 370 | 158 | 259 | -111 | 179 | -33 | 240 | 99.3 | <0.011 |
| 7/27/2006 | 219 | 22000 | 381 | 162 | 337 | -44 | 176 | -43 | 150 | 99.3 | <0.011 |
| 8/1/2006 | 184 | 9000 | 328 | 144 | 275 | -53 | 167 | -17 | 86 | 99.0 | <0.011 |
| 8/3/2006 | 195 | 5400 | 328 | 133 | 251 | -77 | 167 | -28 | 200 | 96.3 | <0.011 |
| 8/8/2006 | 205 | 32000 | 399 | 194 | 302 | -97 | 227 | 22 | 66 | 99.8 | 0.330 |
| 8/10/2006 | 227 | 29000 | 344 | 117 | 276 | -68 | 168 | -59 | 44 | 99.8 | <0.011 |
| 8/15/2006 | 222 | 1300 | 349 | 127 | 269 | -80 | 174 | -48 | 48 | 96.3 | <0.011 |
| 8/17/2006 | 215 | 4100 | 353 | 138 | 256 | -97 | 174 | -41 | 24 | 99.4 | <0.011 |
| 8/22/2006 | 209 | 7000 | 404 | 195 | 277 | -127 | 174 | -35 | 97 | 98.6 | <0.011 |
| 8/24/2006 | 228 | 13000 | 376 | 148 | 281 | -95 | 175 | -53 | 87 | 99.3 | <0.011 |
| 8/29/2006 | 253 | 50000 | 427 | 174 | 346 | -81 | 200 | -53 | 68 | 99.9 | <0.011 |
| 8/31/2006 | 214 | 4400 | 337 | 123 | 246 | -91 | 172 | -42 | 220 | 95.0 | <0.011 |
| 9/5/2006 | 206 | 24000 | 395 | 189 | 300 | -95 | 171 | -35 | 41 | 99.8 | <0.011 |
| 9/7/2006 | 204 | 9700 | 386 | 182 | 251 | -135 | 171 | -33 | 39 | 99.6 | <0.011 |
| 9/12/2006 | 224 | 48000 | 400 | 176 | 259 | -141 | 177 | -47 | 41 | 99.9 | <0.011 |
| 9/14/2006 | 258 | 7900 | 442 | 184 | 313 | -129 | 199 | -59 | 48 | 99.4 | <0.011 |
| 9/19/2006 | 323 | 8600 | 425 | 102 | 379 | -46 | 246 | -77 | 17 | 99.8 | <0.011 |
| 9/21/2006 | 262 | 7400 | 408 | 146 | 312 | -96 | 211 | -51 | 31 | 99.6 | <0.011 |
| 9/26/2006 | 238 | 4000 | 396 | 158 | 277 | -119 | 193 | -45 | 43 | 98.9 | <0.011 |
| 9/28/2006 | 226 | 11000 | 343 | 117 | 274 | -69 | 190 | -36 | 37 | 99.7 | <0.011 |
| 10/3/2006 | 205 | 28000 | 305 | 100 | 240 | -65 | 176 | -29 | 59 | 99.8 | <0.011 |
| 10/5/2006 | 214 | 5600 | 316 | 102 | 273 | -43 | 176 | -38 | 100 | 98.2 | <0.011 |
| 10/10/2006 | 232 | 6200 | 322 | 90 | 286 | -36 | 188 | -44 | 130 | 97.9 | <0.011 |
| 10/17/2006 | 248 | 160000 | 456 | 208 | 416 | -40 | 199 | -49 | 210 | 99.9 | <0.011 |
| 10/19/2006 | 245 | 10000 | 401 | 156 | 348 | -53 | 190 | -55 | 110 | 98.9 | <0.011 |
| 10/24/2006 | 214 | 60000 | 393 | 179 | 369 | -24 | 190 | -24 | 16 | 100.0 | <0.011 |
| 10/26/2006 | 231 | 50000 | 372 | 141 | 341 | -31 | 186 | -45 | 90 | 99.8 | <0.011 |
| 10/31/2006 | 219 | 2600 | 399 | 180 | 354 | -45 | 198 | -21 | 38 | 98.5 | <0.011 |